## Sheet1
INTERLOCK & ALARM LIST_1ST BLOCK
[22 empty] | REVISION | DATE | MADE | CHECK | APPROVAL | CUSTOMER
|  |  | : 해당 사항 |  |  | * PV : Process Value (현재값) |  |  |  |  | AI : Analog Input |  | Condition
| - |  | : 해당 없음 |  |  | * SV : Set Value (설정값) |  |  |  |  | DI : Digital Input |  | *Set : or | [13 empty] | PROJECT NAME
[6 empty] | * MV : Manipulated Value (조작값) | [6 empty] | *Reset : and
DOCUMENT NO.
LCV-01 : Raw Water Pond Level Control Valve
1 | CLOSE BY | [19 empty] | INTERLOCK SIGNAL SOURCE |  | NOTE |  |  | RESULT
| INTERLOCK SET CONDITION | [8 empty] | RESET CONDITION |  |  | SET DELAY |  | RESET DELAY |  | ALARM DELAY |  | SELECT | [6 empty] | BUZZER | LAMP | HMI ALARM | SMS ALARM | INTERLOCK
1 | LIT-01A and LIT-02A or | [5 empty] | Loop Error |  |  | Loop Error Clear -> Reset |  |  | - |  | - |  | - |  | Mode=PLC |  | AI |  | Control Valve Last Value Holding |  |  | - | - |  |  | -
2 | LIT-01B and LIT-02B | [5 empty] | Loop Error |  |  | Loop Error Clear -> Reset |  |  | - |  | - |  | - |  | Mode=PLC |  | AI |  | Control Valve Last Value Holding |  |  | - | - |  |  | -
3
4
5
6
7
8
9
10
REMARK
P&ID PAGE-007
LIT MODE A Pond Mode or B Pond Mode Select
LIT-01A/02A or LIT-01B/02B Loop Error시 Sensor 자동 절체
> A Pond or B Pond Mode Error시 Pond LIT 자동 절체
PID Control Direction (Level Control)
| □ | Forward |  | ■ | Reverse
* Valve Action : Fail Open
RWP-01 : Raw Water Pump
1 | STOP BY | [19 empty] | INTERLOCK SIGNAL SOURCE |  | NOTE |  |  | RESULT
| INTERLOCK SET CONDITION | [8 empty] | RESET CONDITION |  |  | SET DELAY |  | RESET DELAY |  | ALARM DELAY |  | SELECT | [6 empty] | BUZZER | LAMP | HMI ALARM | SMS ALARM | INTERLOCK
1 | 1st Block | [5 empty] | Block Stop |  |  | 1st Block Run |  |  | - |  | - |  | - |  | - |  | HMI |  | 1st Block Stop |  |  | - | - | - | -
2 | EOCR Trip | [5 empty] | EOCR Trip |  |  | EOCR Reset |  |  | t(7s) |  | - |  | - |  | - |  | MCC EOCR |  | Auto Stand-by Change Function |  |  | - | -
3 | Stand-by Select | [8 empty] | - |  |  | - |  | - |  |  |  | - |  | HMI |  |  |  |  | - | - | - | - | -
4 | DMF-RW-01A~I | [5 empty] | DMF=All Stop |  |  | DMF=Service |  |  | - |  | - |  |  |  | - |  | HMI |  |  |  |  | - | - | - | -
5
6
7
8
9
10
REMARK
P&ID PAGE-011
Program Chart 1st Block 참고
EQUIP' NO. |  | ITL NO. |  | BUZZER |  | LAMP |  | HMI ALARM | SMS ALARM | INTERLOCK |  | EQUIP' NO. |  | ITL NO. |  | BUZZER |  | LAMP |  | HMI ALARM |  | SMS ALARM | INTERLOCK |  | EQUIP' NO. | BUZZER | LAMP | HMI ALARM | SMS ALARM | INTERLOCK
Pump-A |  | 1 |  | - |  | - |  | - | -
|  | 2 |  | - |  | -
|  | 3 |  | - |  | - |  | - | - | -
|  | 4 |  | - |  | - |  | - | -
Pump-B |  | 1 |  | - |  | - |  | - | -
|  | 2 |  | - |  | -
|  | 3 |  | - |  | - |  | - | - | -
|  | 4 |  | - |  | - |  | - | -
Pump-C |  | 1 |  | - |  | - |  | - | -
|  | 2 |  | - |  | -
|  | 3 |  | - |  | - |  | - | - | -
|  | 4 |  | - |  | - |  | - | -
Pump-D |  | 1 |  | - |  | - |  | - | -
|  | 2 |  | - |  | -
|  | 3 |  | - |  | - |  | - | - | -
|  | 4 |  | - |  | - |  | - | -
Pump-E |  | 1 |  | - |  | - |  | - | -
|  | 2 |  | - |  | -
|  | 3 |  | - |  | - |  | - | - | -
|  | 4 |  | - |  | - |  | - | -