## INSTRUMENT LIST
데모용 가상 데이터입니다. 실제 프로젝트 자료가 아닙니다. 노란색 DWG No. 열은 도면 매핑으로 채워지는 칸입니다.
NO | TAG | SERVICE | SYSTEM | LOOP GROUP | MAKER | MODEL | MEAS TYPE | RANGE MIN | RANGE MAX | UNIT | SIGNAL | FAULT MODE | PLC | RACK | SLOT | CH | PANEL | TERMINAL | DWG No. | ALARM L | ALARM H | MANUAL FILE | REMARK
1 | AIT-1001 | PRETREATMENT CONDUCTIVITY | PRETREATMENT | PT-TRAIN-A | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 8 | 4 | CUB-B | TB2-37 |  | 13.18 | 88.94 | MT_M300_OM.pdf
2 | PIT-1002 | PRETREATMENT PRESSURE | PRETREATMENT | PT-TRAIN-B | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 7 | 0 | CUB-A | TB6-21 |  | 1.31 | 8.44 | GENERIC_TX_OM.pdf
3 | FIT-1003 | PRETREATMENT FLOW | PRETREATMENT | PT-TRAIN-A | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 2 | 4 | RIO-02 | TB9-30 |  | 5.93 | 42.99 | GENERIC_TX_OM.pdf
4 | TIT-1004 | PRETREATMENT TEMPERATURE | PRETREATMENT | PT-TRAIN-A | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 7 | CUB-A | TB3-14 |  | 7.01 | 68.84 | GENERIC_TX_OM.pdf
5 | AIT-2001 | RO SYSTEM RESISTIVITY | RO SYSTEM | RO-TRAIN-A | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 3 | RIO-02 | TB1-12 |  | 17 |  | MT_M300_OM.pdf
6 | AIT-2002 | RO SYSTEM CONDUCTIVITY | RO SYSTEM | RO-TRAIN-A | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 8 | 4 | RIO-01 | TB1-37 |  | 10.63 | 90.27 | MT_M300_OM.pdf
7 | PIT-2003 | RO SYSTEM PRESSURE | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 3 | 2 | CUB-B | TB5-1 |  | 0.77 | 8.83 | GENERIC_TX_OM.pdf
8 | FIT-2004 | RO SYSTEM FLOW | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 7 | RIO-01 | TB6-4 |  | 4.3 | 42.52 | GENERIC_TX_OM.pdf
9 | LIT-2005 | RO SYSTEM LEVEL | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 1 | CUB-A | TB4-17 |  | 8.94 | 85.86 | GENERIC_TX_OM.pdf
10 | AIT-3001 | CEDI SYSTEM RESISTIVITY | CEDI SYSTEM | CEDI-STACK-1 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 3 | 4 | RIO-01 | TB8-23 |  | 17 |  | MT_M300_OM.pdf
11 | AIT-3002 | CEDI SYSTEM CONDUCTIVITY | CEDI SYSTEM | CEDI-STACK-1 | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 8 | 0 | RIO-01 | TB8-3 |  | 9.68 | 80.05 | MT_M300_OM.pdf
12 | PIT-3003 | CEDI SYSTEM PRESSURE | CEDI SYSTEM | CEDI-STACK-1 | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 6 | 6 | CUB-B | TB5-4 |  | 1.17 | 8.35 | GENERIC_TX_OM.pdf
13 | FIT-3004 | CEDI SYSTEM FLOW | CEDI SYSTEM | CEDI-STACK-1 | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 3 | 1 | RIO-01 | TB5-40 |  | 3.71 | 43.43 | GENERIC_TX_OM.pdf
14 | AIT-4001 | UPW TANK RESISTIVITY | UPW TANK | TANK-01 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 7 | 6 | CUB-B | TB5-1 |  | 17 |  | MT_M300_OM.pdf
15 | AIT-4002 | UPW TANK TOC | UPW TANK | TANK-01 | VEOLIA SIEVERS | M9e | TOC | 0 | 50 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 8 | 3 | RIO-01 | TB5-17 |  |  | 5 | SIEVERS_M9e_OM.pdf
16 | LIT-4003 | UPW TANK LEVEL | UPW TANK | TANK-01 | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 6 | 2 | CUB-A | TB3-12 |  | 12.32 | 90.68 | GENERIC_TX_OM.pdf
17 | TIT-4004 | UPW TANK TEMPERATURE | UPW TANK | TANK-01 | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 6 | CUB-B | TB6-23 |  | 8.02 | 68.05 | GENERIC_TX_OM.pdf
18 | AIT-5001 | POLISHING LOOP RESISTIVITY | POLISHING LOOP | POL-LOOP-1 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 2 | 2 | CUB-B | TB8-35 |  | 17 |  | MT_M300_OM.pdf
19 | AIT-5002 | POLISHING LOOP DISSOLVED OXYGEN | POLISHING LOOP | POL-LOOP-1 | METTLER TOLEDO | M300 | DISSOLVED OXYGEN | 0 | 200 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 5 | 6 | CUB-B | TB5-19 |  | 22.11 | 172.49 | MT_M300_OM.pdf
20 | AIT-5003 | POLISHING LOOP TOC | POLISHING LOOP | POL-LOOP-1 | VEOLIA SIEVERS | M9e | TOC | 0 | 50 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 6 | CUB-B | TB9-32 |  |  | 5 | SIEVERS_M9e_OM.pdf
21 | PIT-5004 | POLISHING LOOP PRESSURE | POLISHING LOOP | POL-LOOP-1 | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 5 | RIO-01 | TB4-18 |  | 0.89 | 8.28 | GENERIC_TX_OM.pdf
22 | FIT-5005 | POLISHING LOOP FLOW | POLISHING LOOP | POL-LOOP-1 | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 7 | CUB-C | TB8-32 |  | 5.24 | 43.08 | GENERIC_TX_OM.pdf
23 | AIT-6001 | DISTRIBUTION RESISTIVITY | DISTRIBUTION | DIST-LOOP-A | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 5 | 2 | RIO-02 | TB8-11 |  | 17 |  | MT_M300_OM.pdf
24 | AIT-6002 | DISTRIBUTION TOC | DISTRIBUTION | DIST-LOOP-A | VEOLIA SIEVERS | M9e | TOC | 0 | 50 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 6 | 6 | RIO-01 | TB8-39 |  |  | 5 | SIEVERS_M9e_OM.pdf
25 | PIT-6003 | DISTRIBUTION PRESSURE | DISTRIBUTION | DIST-LOOP-B | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 7 | 7 | RIO-01 | TB6-11 |  | 1.21 | 9.17 | GENERIC_TX_OM.pdf
26 | FIT-6004 | DISTRIBUTION FLOW | DISTRIBUTION | DIST-LOOP-A | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 6 | 5 | RIO-02 | TB4-34 |  | 5.13 | 42.68 | GENERIC_TX_OM.pdf
27 | TIT-6005 | DISTRIBUTION TEMPERATURE | DISTRIBUTION | DIST-LOOP-B | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 3 | CUB-A | TB7-2 |  | 10.52 | 64.65 | GENERIC_TX_OM.pdf
28 | AIT-7001 | RECLAIM CONDUCTIVITY | RECLAIM | RCL-01 | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 3 | 2 | RIO-02 | TB9-12 |  | 10.19 | 84.7 | MT_M300_OM.pdf
29 | AIT-7002 | RECLAIM pH | RECLAIM | RCL-01 | METTLER TOLEDO | M300 | pH | 0 | 14 | pH | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 4 | RIO-01 | TB4-4 |  | 1.5 | 12.41 | MT_M300_OM.pdf
30 | PIT-7003 | RECLAIM PRESSURE | RECLAIM | RCL-01 | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 6 | CUB-B | TB4-20 |  | 0.88 | 8.78 | GENERIC_TX_OM.pdf
31 | LIT-7004 | RECLAIM LEVEL | RECLAIM | RCL-01 | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 3 | 5 | CUB-B | TB2-36 |  | 11.57 | 87.37 | GENERIC_TX_OM.pdf
32 | AIT-1005 | PRETREATMENT CONDUCTIVITY | PRETREATMENT | PT-TRAIN-A | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 7 | RIO-02 | TB3-19 |  | 12.45 | 81.5 | MT_M300_OM.pdf
33 | PIT-1006 | PRETREATMENT PRESSURE | PRETREATMENT | PT-TRAIN-A | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 4 | RIO-02 | TB3-39 |  | 1.32 | 8.92 | GENERIC_TX_OM.pdf
34 | FIT-1007 | PRETREATMENT FLOW | PRETREATMENT | PT-TRAIN-A | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 4 | 7 | CUB-B | TB7-28 |  | 4.43 | 42.53 | GENERIC_TX_OM.pdf
35 | TIT-1008 | PRETREATMENT TEMPERATURE | PRETREATMENT | PT-TRAIN-B | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 1 | CUB-A | TB7-10 |  | 11.06 | 68.06 | GENERIC_TX_OM.pdf
36 | AIT-2006 | RO SYSTEM RESISTIVITY | RO SYSTEM | RO-TRAIN-A | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 7 | 0 | CUB-B | TB9-38 |  | 17 |  | MT_M300_OM.pdf
37 | AIT-2007 | RO SYSTEM CONDUCTIVITY | RO SYSTEM | RO-TRAIN-B | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 5 | 7 | CUB-A | TB8-9 |  | 11.85 | 81.43 | MT_M300_OM.pdf
38 | PIT-2008 | RO SYSTEM PRESSURE | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 6 | 4 | CUB-B | TB5-17 |  | 0.85 | 8.72 | GENERIC_TX_OM.pdf
39 | FIT-2009 | RO SYSTEM FLOW | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 0 | RIO-01 | TB7-16 |  | 2.67 | 43.15 | GENERIC_TX_OM.pdf
40 | LIT-2010 | RO SYSTEM LEVEL | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 4 | CUB-A | TB3-34 |  | 11.33 | 90.13 | GENERIC_TX_OM.pdf
41 | AIT-3005 | CEDI SYSTEM RESISTIVITY | CEDI SYSTEM | CEDI-STACK-1 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 5 | CUB-B | TB8-10 |  | 17 |  | MT_M300_OM.pdf
42 | AIT-3006 | CEDI SYSTEM CONDUCTIVITY | CEDI SYSTEM | CEDI-STACK-1 | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 6 | CUB-A | TB1-21 |  | 14.59 | 86.47 | MT_M300_OM.pdf
43 | PIT-3007 | CEDI SYSTEM PRESSURE | CEDI SYSTEM | CEDI-STACK-1 | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 5 | CUB-A | TB3-17 |  | 1.38 | 9.08 | GENERIC_TX_OM.pdf
44 | FIT-3008 | CEDI SYSTEM FLOW | CEDI SYSTEM | CEDI-STACK-1 | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 3 | 7 | CUB-C | TB6-30 |  | 3.76 | 44.46 | GENERIC_TX_OM.pdf
45 | AIT-4005 | UPW TANK RESISTIVITY | UPW TANK | TANK-01 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 1 | 3 | CUB-A | TB9-27 |  | 17 |  | MT_M300_OM.pdf
46 | AIT-4006 | UPW TANK TOC | UPW TANK | TANK-01 | VEOLIA SIEVERS | M9e | TOC | 0 | 50 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 2 | 0 | CUB-B | TB3-19 |  |  | 5 | SIEVERS_M9e_OM.pdf
47 | LIT-4007 | UPW TANK LEVEL | UPW TANK | TANK-01 | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 4 | 6 | RIO-01 | TB8-3 |  | 11.39 | 82.28 | GENERIC_TX_OM.pdf
48 | TIT-4008 | UPW TANK TEMPERATURE | UPW TANK | TANK-01 | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 8 | 1 | CUB-B | TB7-10 |  | 8.93 | 71.55 | GENERIC_TX_OM.pdf
49 | AIT-5006 | POLISHING LOOP RESISTIVITY | POLISHING LOOP | POL-LOOP-1 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 1 | 1 | RIO-01 | TB5-28 |  | 17 |  | MT_M300_OM.pdf
50 | AIT-5007 | POLISHING LOOP DISSOLVED OXYGEN | POLISHING LOOP | POL-LOOP-1 | METTLER TOLEDO | M300 | DISSOLVED OXYGEN | 0 | 200 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 2 | 7 | CUB-A | TB4-28 |  | 11.49 | 179.24 | MT_M300_OM.pdf
51 | AIT-5008 | POLISHING LOOP TOC | POLISHING LOOP | POL-LOOP-1 | VEOLIA SIEVERS | M9e | TOC | 0 | 50 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 6 | 6 | CUB-C | TB4-35 |  |  | 5 | SIEVERS_M9e_OM.pdf
52 | PIT-5009 | POLISHING LOOP PRESSURE | POLISHING LOOP | POL-LOOP-1 | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 2 | CUB-B | TB3-30 |  | 1.5 | 8.96 | GENERIC_TX_OM.pdf
53 | FIT-5010 | POLISHING LOOP FLOW | POLISHING LOOP | POL-LOOP-1 | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 2 | 6 | CUB-A | TB2-10 |  | 6.19 | 42.74 | GENERIC_TX_OM.pdf
54 | AIT-6006 | DISTRIBUTION RESISTIVITY | DISTRIBUTION | DIST-LOOP-A | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 8 | 1 | RIO-02 | TB2-30 |  | 17 |  | MT_M300_OM.pdf
55 | AIT-6007 | DISTRIBUTION TOC | DISTRIBUTION | DIST-LOOP-B | VEOLIA SIEVERS | M9e | TOC | 0 | 50 | ppb | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 2 | 3 | CUB-B | TB9-19 |  |  | 5 | SIEVERS_M9e_OM.pdf
56 | PIT-6008 | DISTRIBUTION PRESSURE | DISTRIBUTION | DIST-LOOP-A | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 5 | CUB-B | TB3-2 |  | 0.66 | 8.72 | GENERIC_TX_OM.pdf
57 | FIT-6009 | DISTRIBUTION FLOW | DISTRIBUTION | DIST-LOOP-B | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 6 | 3 | CUB-A | TB1-6 |  | 6.11 | 41.34 | GENERIC_TX_OM.pdf
58 | TIT-6010 | DISTRIBUTION TEMPERATURE | DISTRIBUTION | DIST-LOOP-B | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 2 | 0 | RIO-02 | TB6-29 |  | 4.01 | 67.94 | GENERIC_TX_OM.pdf
59 | AIT-7005 | RECLAIM CONDUCTIVITY | RECLAIM | RCL-01 | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 6 | 6 | CUB-C | TB4-27 |  | 13.82 | 86.48 | MT_M300_OM.pdf
60 | AIT-7006 | RECLAIM pH | RECLAIM | RCL-01 | METTLER TOLEDO | M300 | pH | 0 | 14 | pH | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 2 | 5 | CUB-A | TB2-11 |  | 2 | 11.22 | MT_M300_OM.pdf
61 | PIT-7007 | RECLAIM PRESSURE | RECLAIM | RCL-01 | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 3 | 1 | CUB-B | TB9-40 |  | 0.89 | 8.18 | GENERIC_TX_OM.pdf
62 | LIT-7008 | RECLAIM LEVEL | RECLAIM | RCL-01 | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 7 | 6 | CUB-A | TB8-34 |  | 6.62 | 91.04 | GENERIC_TX_OM.pdf
63 | AIT-1009 | PRETREATMENT CONDUCTIVITY | PRETREATMENT | PT-TRAIN-A | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 5 | 2 | CUB-B | TB3-31 |  | 6.91 | 87.88 | MT_M300_OM.pdf
64 | PIT-1010 | PRETREATMENT PRESSURE | PRETREATMENT | PT-TRAIN-B | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 4 | 1 | RIO-02 | TB8-5 |  | 0.7 | 8.16 | GENERIC_TX_OM.pdf
65 | FIT-1011 | PRETREATMENT FLOW | PRETREATMENT | PT-TRAIN-B | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 4 | 0 | CUB-C | TB1-1 |  | 3.02 | 44.02 | GENERIC_TX_OM.pdf
66 | TIT-1012 | PRETREATMENT TEMPERATURE | PRETREATMENT | PT-TRAIN-A | GENERIC | TX-2000 | TEMPERATURE | 0 | 80 | degC | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 2 | CUB-A | TB4-13 |  | 4.04 | 67.42 | GENERIC_TX_OM.pdf
67 | AIT-2011 | RO SYSTEM RESISTIVITY | RO SYSTEM | RO-TRAIN-A | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 1 | 6 | CUB-A | TB8-9 |  | 17 |  | MT_M300_OM.pdf
68 | AIT-2012 | RO SYSTEM CONDUCTIVITY | RO SYSTEM | RO-TRAIN-B | METTLER TOLEDO | M300 | CONDUCTIVITY | 0 | 100 | uS/cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 2 | 5 | CUB-C | TB6-5 |  | 14.3 | 84.01 | MT_M300_OM.pdf
69 | PIT-2013 | RO SYSTEM PRESSURE | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | PRESSURE | 0 | 10 | bar | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 7 | 6 | RIO-01 | TB3-40 |  | 1.16 | 8.2 | GENERIC_TX_OM.pdf
70 | FIT-2014 | RO SYSTEM FLOW | RO SYSTEM | RO-TRAIN-A | GENERIC | TX-2000 | FLOW | 0 | 50 | m3/h | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 7 | RIO-02 | TB3-26 |  | 4.3 | 45.33 | GENERIC_TX_OM.pdf
71 | LIT-2015 | RO SYSTEM LEVEL | RO SYSTEM | RO-TRAIN-B | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 5 | 5 | CUB-C | TB7-40 |  | 13.58 | 86.98 | GENERIC_TX_OM.pdf
72 | AIT-3009 | CEDI SYSTEM RESISTIVITY | CEDI SYSTEM | CEDI-STACK-1 | METTLER TOLEDO | M300 | RESISTIVITY | 0 | 18.2 | Mohm-cm | 4-20mA AI | Upscale 22mA (self-diag) | PLC-UPW-01 | 0 | 4 | 4 | RIO-01 | TB5-24 |  | 17 |  | MT_M300_OM.pdf
73 | LIT-01A | RAW WATER POND A LEVEL | PRETREATMENT | POND-A | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 0 | CUB-A | TB9-1 |  |  |  | GENERIC_TX_OM.pdf | INTERLOCK_SAMPLE LCV-01 조건 태그 (데모)
74 | LIT-01B | RAW WATER POND B LEVEL | PRETREATMENT | POND-B | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 1 | CUB-A | TB9-3 |  |  |  | GENERIC_TX_OM.pdf | INTERLOCK_SAMPLE LCV-01 조건 태그 (데모)
75 | LIT-02A | RAW WATER POND A LEVEL (REDUNDANT) | PRETREATMENT | POND-A | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 2 | CUB-A | TB9-5 |  |  |  | GENERIC_TX_OM.pdf | INTERLOCK_SAMPLE LCV-01 조건 태그 (데모)
76 | LIT-02B | RAW WATER POND B LEVEL (REDUNDANT) | PRETREATMENT | POND-B | GENERIC | TX-2000 | LEVEL | 0 | 100 | % | 4-20mA AI | Downscale <3.6mA (NAMUR) | PLC-UPW-01 | 0 | 1 | 3 | CUB-A | TB9-7 |  |  |  | GENERIC_TX_OM.pdf | INTERLOCK_SAMPLE LCV-01 조건 태그 (데모)